Petascale Systems Integration into Large Scale Facilities Workshop Report

Draft 1.0 – August 31, 2007

San Francisco, California

May 15-16, 2007

Workshop Sponsors: DOE Office of Science – ASCR

Workshop Organizer: William T.C. Kramer – NERSC

Report Author – William T.C. Kramer – NERSC

Report Editors – Ucillia Wang, Jon Bashor

Workshop Attendees/Report Contributors:

Bill Allcock, Anna Maria Bailey, Ron Bailey, Ray Bair, Ann Baker, Robert Balance, Jeff Becklehimer, Tom Bettge, Richard Blake, Buddy Bland, Tina Butler, Nicholas Cardo, Bob Ciotti, Susan Coghlan,

Brad Comes, Dave Cowley, Kim Cupps, Thomas Davis, Daniel Dowling, Tom Engel, Al Geist, Richard Gerber, Sergi Girona, Dave Hancock, Barbara Helland, Dan Hitchcock, Wayne Hoyenga, Fred Johnson, Gary Jung, Jim Kasdorf, Chulho Kim, Patricia Kovatch, William T.C. Kramer, Paul Kummer, Steve Lowe,Tom Marazzi, Dave Martinez, Mike McCraney, Chuck McParland,

Stephen Meador, George Michaels,

Tommy Minyard, Tim Mooney, Wolfgang E. Nagel, Gary New,

Rob Pennington, Terri Quinn, Kevin Regimbal, Renato Ribeiro,

Lynn Rippe, Jim Rogers, Jay Scott, Mark Seager, David Skinner, Kevin Stelljes, Gene Stott, Sunny Sundstrom, Bob Tomlinson, Francesca Verdier, Wayne Vieira,

Howard Walter, Ucilia Wang, Harvey Wasserman, Kevin Wohlever, Klaus Wolkersdorfer

Summary

There are significant issues regarding Large Scale System integration that are not being addressed in other forums, such as the current research portfolios or vendor user groups. The impact of less-than-optimal integration technology means the time required to deploy, integrate and stabilize large scale system may consume up to 25 percent of the useful life of such systems. Therefore, improving the state of the art for large scale systems integration has potential for great impact by increasing the scientific productivity of these systems.

Sites have a great deal of expertise, but there are not easy ways to leverage this expertise between sites. Many issues get in the way of sharing informatoin, including available time and effort, as well as issues involved with sharing proprietary information. Vendors also benefit in the long run from the issues detected and solutions found during site testing and integration. Unfortunately, the issues in the area of large scale system integration often fall between the cracks of research, user services and hardware procurements.

There is a great deal of enthusiasm for making large scale system integration a full-fledged partner along with the other major thrusts supported by the agencies in the definition, design, and use of a petascale systems. Integration technology and issues should have a full “seat at the table” as petascale and exascale initiatives and programs are planned.

The workshop attendees identified a wide range of issues and suggested paths forward. Pursuing these with funding opportunities and creative innovation offer the opportunity to dramatically improve the state of large scale system integration.

Introduction

As high-performance computing vendors and supercomputing centers move toward petascale computing, every phase of these systems, from the first design to the final use, presents unprecedented challenges. Activity is underway for requirements definition, hardware and software design, programming models modifications, methods and tools innovation and acquisitions. After systems are designed and purchased, and before they can be used at petascale for their intended purposes, they must be installed in a facility, integrated with the existing infrastructure and environment, tested and then deployed for use. Unless system testing and integration is done effectively, there are risks that large scale systems will never reach their full potential.

In order to help lay the foundation for successful deployment and operation of petascale systems, the National Energy Research Scientific Computing Center at Lawrence Berkeley National Laboratory hosted a two-day workshop on “Petascale Systems Integration into Large Scale Facilities.” Sponsored by DOE’s Office of Advanced Scientific Computing Research (ASCR), the workshop examined the challenges and opportunities that come with petascale systems deployment. Nearly 70 participants from the U.S and Europe, representing 29 different organizations, joined the effort to identify the challenges; search for the best practices; share experiences and define lessons learned. The workshop assessed the effectiveness of tools and techniques that are or could be helpful in petascale deployments, and sought to determine potentially beneficial tools areas for research and development. The workshop also addressed methods to ensure systems continue to operate and perform at equal or better levels throughout their lifetime after deployment. Finally, the workshop sought to add the collective experience and expertise of the attendees to the HPC community’s body of knowledge, as well as foster a network of experts who are able to share information on an ongoing basis as petascale systems come on line.

Specifically, the goals of the workshop were to:

- Identify challenges and issues involved in the installation and deployment of large scale HPC systems

- Identify best practices for installing large-scale HPC systems into scientific petascale facilities

- Identify methods to assure system performance and function continue after initial testing and deployment

- Identify systematic issues and research issues for vendors, sites and facilities that would improve the speed and quality of deployment

- Share tools and methods that are helpful in expediting the installation, testing and configuration of HPC systems

- Establish communication paths for technical staff at multiple sites that might make HPC installations more effective

- Make recommendations to DOE and other stakeholders to improve the process of HPC system deployment

Workshop Priority Summary Findings and Recommendations (Sub recommendations are in italics)

The workshop participants developed many suggestions in the course of their exploration. However, the workshop participants evaluated the priorities for all the recommendations and agreed on the highest priority ones that will determine the success of petascale systems. These highest priority items are summarized below.

- Improve the ability to record and process log data.

Recommendation:There will be a tremendous amount of logging data about system use and system status. There needs to be new ways process this data – in real time. Specific improvements are:

- Develop common log data models and data formats that enable integrated analysis tools and easier sharing

- Develop consolidation of events

- Increase the amount of “Intelligent” logging – ala the AMR tool – that do broad analysis with automated detailed focus as needed.

- Increase the site’s and vendors’ ability to do forensic analysis

The vendors and sites are most likely to make progress in this area since there is a large amount of detailed knowledge and context needed.

Recommendation: Share tools and system integration and operational data across sites. This will enable the ability to look for larger trends. Six sites agreed to share current data at the workshop with others indicating a willingness to consider sharing. Sharing of data also enables understanding different systems and codes behavior. In order to accomplish this recommendation the following must happen.

- A common/standard format needs to be defined.

- There will probably be a need to develop tools to convert from proprietary and/or current formats to the standard format.

- It is important to look at the entire data model of log file analysis rather than just a common format. This means involving expertise in data management, curation and data protection.

- This single effort, if attempted seriousl,y would require an entire workshop – or a series of workshops to make progress.

Recommendation: Build a repository of log files first in order to start building tools. At the workshop, eight sites agreed to share system log data (but under an agreement that the data would not be further shared) and Indiana University agreed to host the site, which the participating facilities would be responsible for creating. Steps to achieve this recommendation include

- Defining the data models and low level information to be captured.

- Make data model extensible since unanticipated and new data may become available. It also includes performing research in how to sanitize logs in order to release them to the general academic community for further contributions.

- Analysis tools need to be developed. There should be an effort to look at applying statistical analysis to data (see LANL).

- An initial, very useful tool would be to use the Simple Event Correlator – an open source package – to analyze events.

- Create improved methods to visualize the system state.

This recommendation overlaps some of the security logging issues developed at the February Security Workshop.

- The ability to have multiple versions of system software on the petascale systems.

Recommendation:It is important to be able to test system software at scale and to be able to quickly go back and forth between versions of software. This includes the entire software stack and microcode. If there were system software transition requirements in RFP’s for being able to switch between software levels, would vendors be able to provide a response. Two sites do include such system software switching requirements in their RFPs, about 6 would consider adding such a requirement. Sites suggested sharing RFPs so they can learn from each other

It would be beneficial if there a way for vendors to isolate system level software changes to provide limited test environments. One problematic areas is being able to separate firmware upgrades from system software upgrades. In many cases today, if firmware is upgraded, older software versions can not be used. Having the ability to partition the system, including the shared file system without the cost of replicating all the hardware would be very helpful in many cases.

- Have better hardware and software diagnostics

Recommendation: Better proactive diagnostics are critical to getting systems into service on time and at the expected quality. Vendors are responsible for providing diagnostics with the goal of having the diagnostics able to determine root causes. One very important requirement is to be able to run diagnostics without taking the entire system down into dedicated mode.

Better definition is needed before vendors can develop better tools. There is a difference between testing and diagnostics. Testing is the process of trying to decide if there is a problem. Diagnostics should be used to diagnose the system once it is known that there is a problem. Diagnostics should be able to point to a field replaceable unit so a repair action can take place. Diagnostics should be created for all software as well as hardware.

To improve the areas of diagnostics, the HPC community and vendors have to work together to determine what already exists, prioritize what tools are needed and determine what can be done with system administration issues and with hardware issues.

Recommendation:HPC systems need shorter MTTR. The vendors at the workshop indicated that if sites put MTTR requirements into RFPs to define the requirements for vendorsm the vendor community, over time, could respond with specific improvements.

But, currently, it is unclear what can be specified and the best manner to do so.

All sites want on-line diagnostics to be as comprehensive as off-line diagnostics. Sites also desire the ability to analyze soft errors to predict problems rather than just correcting for them. There is also a need to test diagnostics as part of an acceptance test, but this process is not at all clear, other than to observe their use during acceptance.

- I/O Activity and Analysis Tools

Recommendation: Data is a bigger and bigger issue and will possibly become unmanageable at the petascale. For example, some sites are taking more than a week to backup large file systems using the methods supplied by vendors. It is harder and harder to get parallel data methods right for performance.

In order to manage the aggregate data available on these systems, better information for what is going on at any moment is necessary. Storage system tools that are the equivalent to HPM/PAPI for CPU performance data gathering are needed. Where tools do exist, there is a wide variance in what they do and no common standards for data.

There are two purposes for monitoring and understanding data from storage systems. The first is to diagnosis code performance. This will enable the creation of new tools that can be used for application I/O performance understanding and improvement. Early tools of this type are being developed at Dresden ZIH. The second reason is to determine system performance and enable system managers to tune the system for the overall workload. This data would also make it easier for data system designers to make improvements in data systems.

There are significant challenges concerning how to get to the information that are in many layers of the systems. Visualizing and correlating I/O system data is not trivial. Today’s data tools mostly test point-to-point performance. They are lacking in being able to monitor and assess overall system behavior, true aggregate performance and conflicting use and demands. Many sites, including NERSC, LBNL, ORNL, SNL, LANL and LLNL are working on this in different ways, using tools such as IOR and AMR I/O benchmarks.

There should be another workshop focused on this issue.

- Peer Interactions and Best Practices

In the past, the facility and building staff at major HPC facilities have not had the opportunity for detailed technical interactions to exchange practices. HPC facility management differs from other building management in significant ways, not the least being the rate of change that occurs with new technology being incorporated into the building. Petascale will stress facilities, even specially designed facilities. Having facility manager peers brainstorm before designs and major changes to assure all issues are covered and the latest approaches are taken is critical to the ability of facilities to operate close to the margins.

There is a large history of sharing performance data but not a tradition for other data such as reliability, software and hardware problems, security issues and user issues. Now all sites are multi-vendor sites. Sharing of problem reports (SPRs) for systems is something that is not being done across sites. This was a common practice in formal organizations such as user groups, which to large degrees have become less effective in this manner. Sites have many more vendors these days so there is no single (or even a few) places to share information. Furthermore, no mechanism exists to share problem information across vendor-specific systems. Such information sharing is not deemed appropriate for research meetings so rarely appears on the agenda. In some cases, vendors actively inhibit sharing of problems reports, so facilitating community exchange is critical to success.

Similar issues exist when systems are going through acceptance at different sites. While this may be more sensitive, some form of sharing may be possible. Even having a summary report of the experiences of each large system installation after integration would be useful. There should be a common place to post these reports, but access must be carefully controlled so vendors are not afraid to participate. For facilities-specific issues, the APCOM Facility conference may have some value.

As a mark of the need and interest in this area, some sites already mark their SPRs public rather than private when possible. Five sites expressed willingness to share their SPRs if a mechanism existed, and more indicated they would consider it.

In order to have increased study of this area and generate wider participation, it may be useful to explore a special journal edition devoted to Large Scale System Integration. Likewise, creating an on-line community, euphemistically labeled “HPC_space.com” by the attendees, will provide the ability to share more real time issues through mechanisms such as twikis or blogs. However, the “rules of engagement” need to be carefully considered to consider the needs of vendors, systems, areas of interest and sites. Look at Instructions to America that create communities of practice on many topics.

- Tools for Understanding Performance and Function for storage (disk) management and reliability and other Key components.

Tools need to be developed to better move and manage data. Other tools are needed to get information from data. Data insight tools should operate in real time with application improvements. The storage community is working on improved tools to manage data, and some of these are already being included in SciDAC projects.. The science research community can and should deal with the performance of small data writes and new ways to handle very large numbers of files. Vendors and others are dealing with Information Lifecycle Management, including hierarchies of data movement. They also should provide the ability to monitor large numbers of storage and fabric devices as well as tools for disk management.

Other key components are to create tools for understanding interconnects such as PAPI/IPM and performance profiling tools for other programming models such as PGAS languages.

- Parallel Debuggers

Parallel debuggers can be a significant help with integration issues as well as help users be more productive. It is not clear that sites understand how users debug their large codes. Although this topic was partly covered at a DOE-sponsored workshop on petascale tools in August 2007, it is not clear there is a connection with the Integration Community

Additional key observations were made by the attendees.

All sites face many similar integration issues, regardless of the vendors providing the systems. Many issues identified during the workshop span vendors, and hence are persistent. Vendors will never see the number and diversity of the problems that are seen during integration at sites because they concentrate only on the issues that are immediately impacting their systems. There currently is no forum to deal with applied issues of large scale integration and management that span vendors.

The problem of integrating petascale systems is too big for any one site to solve. The systems are too big and complex for a single workload to uncover all the issues. Often just fully understanding problems is a challenge that takes significant effort. Increased use of open and third party software makes each system unique and compounds the problem. Funding agencies are not yet willing to fund needed improvements in this area of large scale integration since it is not fit into the normal research portfolio.

Site priorities need to apply to acceptance and integration decisions rather than vendor priorities for when and how systems are to be considered ready for production. It would be useful to create a framework for sites to do the quality assurance that can be used by vendors in pre-installation checklists. The competition between sites should not be allowed to get in the way of improving integration methods.

A number of suggestions for post workshop activities were made. One is to create an infrastructure for continuing the momentum made in this workshop. Another is to provide further forums/formats for future events that continue to address these issues. It may be possible to follow on with a workshop at SC 07 and PNNL is willing to help organize this.

NSF indicated they believe more collaboration is needed in this area of large scale integration. Many pressures are involved with fielding large scale systems. Cost pressures come from electrical costs increasing dramatically and the costs to store data will “eat us alive” as the community goes to petascale unless data and cost issues are addressed systematically.

Some systematic problems prevent more rapid quality integration. Areas that need additional work and more detailed investigation are interconnects, I/O, large system OS issues and facilities improvements. Having system vendors at this first workshop was very beneficial, but future meetings should also include interconnect and storage vendors.

The basic question remains, “Have we looked far enough in advance or are we just trying solving the problems we have already seen?” It is not clear this the case, but the findings and recommendations of the workshop are an excellent starting point.

Workshop Overview

The two-day meeting in San Francisco attracted about 70 participants from roughly 30 supercomputer centers, vendors, other research institutions and DOE program managers The discussions covered a wide-range of topics, including facility requirements, integration technologies, performance assessment, and problem detection and management. While the attendees were experienced in developing and managing supercomputers, they recognized that the leap to petascale computing requires more creative approaches.

“We are going through a learning curve. There is fundamental research to be done because of the change in technology and scale,” said Bill Kramer, NERSC’s General Manager who led the workshop.

In his welcoming remarks, Dan Hitchcock, Acting Director of the Facilities Division within ASCR, urged more collaboration across sites fielding large scale systems, noting that various stakeholders in the high-performance computing community have historically worked independently to solve thorny integration problems.

Mark Seager from Lawrence Livermore National Laboratory and Tom Bettge from the National Center for Atmospheric Research (NCAR) helped kick-start the workshop by sharing their experiences with designing state-of-the-art computer rooms and deploying their most powerful systems. Both Seager and Bettge said having sufficient electrical power to supply massive supercomputers is becoming a major challenge. A search for more space and reliable power supply led NCAR to Wyoming, where it will partner with the state of Wyoming and the University of Wyoming to build a $60-million computer center in Cheyenne. One of the key factors in choosing the location is the availability of stable electrical power. (Interestingly, the stability comes as much from the fact there is a WalMart refrigeration plant nearby that draws 9 MW of power)

Seager advocated the creation of a risk management plan to anticipate the worst-case scenario. “I would argue that the mantra is ‘maximizing your flexibility,’” Seager said. “Integration is all about making lemonade out of lemons. You need a highly specialized customer support organization, especially during integration.”

Six breakout sessions took place over the two days to hone in on specific issues, such as the best methods for performance testing and the roles of vendors, supercomputer centers and users in ensuring the systems continue to run well after deployment.

The workshop program included a panel of vendors offering their views on deployment challenges. The speakers, representing IBM, Sun Microsystems, Cray and Linux Networx, discussed constraints they face, such as balancing the need to invest heavily in research and development with the pressure to make profit.

A second panel of supercomputer center managers proffered their perspectives on the major hurdles to overcome. For example, Patricia Kovatch from the San Diego Supercomputer Center hypothesized that the exponential growth in data could cost her center $100 million a year for petabyte tapes in order to support a petascale system unless new technology is created. Currently the center spends about $1 million a year on tapes.

“We feel that computing will be driven by memory, not CPU. The tape cost is a bigger problem than even power,” Kovatch told attendees.

The amount and performance of computer memory is clearly one of many challenges. Leaders from each breakout sessions presented slides detailing the daunting tasks ahead, including software development, acceptance testing and risk management.

Breakout Session Summaries

Charge to Breakout Group #1: Integration Issues for Facilities

Petascale systems are pushing the limits of facilities in terms of space, power, cooling and even weight. There are many complex issues facility managers must deal with when integrating large scale systems and these will get more challenging with Petascale systems. Example issues the break could address:

- While we all hope technology will reverse these trends, can we count on it?

- Besides building large facilities (at Moore’s Law rates) how can we better optimize facilities?

- How can the lead times and costs for site preparation be reduced?

- Can real time adjustments be made rather than over design?

Report of Break Out Group #1

The discussion covered three major scenarios:

- Designing a new building

- Planning of facilities

- Upgrading an existing facility

Designing a new building

Although participants agreed that designing a new building with extensive infrastructure up front can significantly reduce long term costs, this is quite a challenge when the machines to be procured and deployed are not known during the design phase. However, the cost savings can be substantial.

Computing facilities have several aspects that do not exist in standard building projects. The most obvious is the rate of change computing buildings must support due to the rapid technology advances associated with Moore’s Law and computing. It is typical for a computing facility to receive major new equipment every two to three years. It is also typical that the entire computing complex turns over in 6 to 8 years. This new equipment makes substantial demands on building infrastructure. As with construction, the cost to retrofit can far exceed the cost of original implementation.

Another difference in computing facilities for the giga-, tera- and petascale is there areexpected to be significant changes in cooling technology, with cycles of air cooling and liquid cooling cycling once every 10 to 15 years. Standard buildings have a 30 to 50 year life cycles. Unless designed to be highly flexible, computing facilities will have to be built on a much shorter time cycle.

One important recommendation is to close the gap between systems and facilities staff at centers. This could help each center develop a planning matrix to determine the correlation between major categories of integrating effort and cost to the system technology.

- Space

- Power

- Cooling

- Networking

- Storage

Each category is a determination of cost vs. benefit and mission vs. survival. What are the tradeoffs in terms of costs vs. benefits? What are the most painful areas of upgrade later in the facility’s lifecycle. What is the anticipated life of the facility? How many procurement cycles are going to be involved with this facility? What is the scope of major systems and the associated storage?

Each organization will need to make its own determination of what they are willing and/or able to fund at a given point in time. With petascale facilities, consideration needs to be given to the equipment itself, regardless of the mission it performs. Underlying these decisions is a need to protect the investment in the system.

Petascale integration requires that all things be considered during the planning phases of all projects. The end game must be considered to determine what level of infrastructure investment needs to be made up front. Invariably, decisions need to be made on a “pay me now or pay me later” basis. If later, the price could be considerably higher. For example, major power feeders and pipe headers should be installed up front to reduce costs later. Designating locations for future plumbing and conduit runs during initial design may require relocation of rebar or other components in the design, but this avoids having to drill through them in the future. Designing and building in a modular fashion, such as installing pads, conduit, etc. in advance, can also reduce future costs and disruptions. In summary, flexibility should be a very significant factor in the cost and effort of creating and re-designing these sites.

Serious consideration needs to be given to value engineering. When items are cut during design, it needs to be understood what the ramifications of the cuts are on the long-term costs of the facility. It has been proven that forward engineering yields significant cost savings down the road.

On the other hand, upgrading existing facilities typically involves a number of difficult retrofitting tasks. These include drilling, digging and jack-hammering; moving large water pipes; removing asbestos; increasing a raised floor. Currently, a raised floor of 36 inches is considered minimum by the group for a large scale facility, with 48inches (or more) preferred. Issues like floor loading can be factors as newer, denser systems appear. Upgrading the facility, whether in terms of infrastructure or computing resources, can also tax users if existing systems in service are disrupted. An overlap of available systems, such as keeping an existing machine in service while an older one is removed to make way for a newer one, can provide uninterrupted access for users but means there needs to be a buffer of facilities and services available (floor space, electrical power, cooling, etc.). An interesting question should what should the facilities design cycle be – 100 percent all the time? 100 percent duty cycle systems require a reduction in other parameters such as quality of service, reliability, utilization, etc.

There is a desire to see better interaction with vendors and facilities to determine and share the direction of new systems (shared knowledge base). One suggestion is to invite peer center personnel to review building design plans to get as much input as possible before and during design, which capitalizes on lessons learned and benefits all participants. Another recommendation is to have a computer technical facility present as part of the facility design and construction team during the entire process.

Environmental Issues

Power consumption and, conversely, power conservation by computing centers is becoming an increasingly important consideration in determining the total cost of ownership as HPC systems grow larger and more powerful. The group noted that new tools and technologies could help in this area. These include:

- Good CFD monitoring tools to better identify hotspots and other problems.

- Monitoring systems that are better integrated with the “controls” for responding to events, including a 3D sensor net monitoring system throughout the entire facility.

- Better tools for monitoring system hardware.

- Better tools for environmental monitoring on a finer grain basis.

Here are some additional observations/suggestions/issues concerning environmental designs.

Cooling

- Cooling office space using different (and possibly more efficient) systems than the machine room should be considered. Maintaining the environment in the machine room is paramount since the lifespan of systems can be reduced due to thermal events. Vendors typically can charge extra for issues stemming from poor environments.

- Liquid cooling will likely make a comeback for petascale systems, but some combination of air and liquid cooling will be required for all systems. In particular, it is unlikely that immersive cooling will return so memory storage and interconnects will remain air cooled in the future.

- Water cooling has an extremely low tolerance for cooling outages or fluctuations.

- Under-floor partitions or other design options should be considered when mixing systems with high and low cooling requirements in a common area.

- At some point, internals of air-cooled hardware will “melt down” if cooling/power is lost with no spinning fans to remove hot air. Technology and design has to ensure that chilled water continues flowing during these events.

- Chiller sequencing problems for redundant chillers during momentary and multiple momentary power interruptions can cause chillers to get into “loops” where neither will start. Some solutions may be cold water reservoir systems, very large water header pipes and rotary systems.

Power

- 480V systems are coming. Facilities may need to make this a requirement for vendor bids to be considered due to prohibitive costs for copper and other power transforming components. There are issues with transient suppression at this level of voltage that do not currently have commercial solutions.

- Is AC and DC power distribution practical/possible? Why are many vendors not in favor of DC power for practical reasons.

- Commodity computing data centers (such as. Google’s facilities) may be designed in a more modular fashion due to the uniformity of racks and components. Petascale facilities have fewer options in regard to generator and UPS backup power. Some group members expressed that their UPS backs up only “single point of failure” components.

- Flywheel power conditioning was discussed. Reliability issues are a concern. Perhaps use of this technology for mechanical equipment is practical, but there is little formal study of this.

- There was a suggestion to move major network components onto UPS backup because routers and switches are non-tolerant of momentary power interruptions.

- Close the gap between systems and facilities staff at centers.

- Invite peer center personnel to review building design plans to get as much input as possible, which capitalizes on lessons learned and benefits all participants.

- Have a project manager from your facility participate in the entire planning process.

Charge to Breakout Group 2: Performance Assessment of Systems

There are many tools and benchmarks that help assess performance of systems, ranging from single performance kernels to full applications. Performance tests can be kernels, specific performance probes and composite assessments. What are the most effective tools? What scale tests are needed to set system performance expectations and to assure system performance? What are the best combinations of tools and tests?

Report of Break Out Group #2

Benchmarks and system tests not only have to evaluate potential systems for evaluation, but then must be able to ensure selected systems perform as expected both during and after acceptance. The challenges in this develop into three primary categories:

1.) Traditional performance metrics fail to adequately capture important characteristics that are increasingly important for both existing supercomputers and emerging petascale systems; such characteristics include space, power, cooling, reliability and consistency. However, the team noted that any new metrics must properly reflect real application performance, during both procurement and system installation. Precise benchmarking is needed to emphasize the power consumed doing “useful work,” rather than peak flops/watt or idle power.

2.) Although some researchers have had success with performance modeling, there remain significant challenges in setting reasonable performance expectations for broadly diversified workloads on new systems in order to realistically set accurate expectations for performance at all stages of system integration. This is particularly important when trying to isolate the cause of performance problems as system testing uncovers problems.

3.) There is a challenge associated with deriving benchmark codes capable of adequately measuring — and reporting in a meaningful way — performance in an increasingly diverse architectural universe that spans the range from homogeneous, relatively low-concurrency systems with traditional “MPI-everywhere” programming models, to hugely concurrent systems that will embody many-core nodes, to heterogeneous systems of any size that include novel architectural features such as FPGA. The key element in all of these is the need to have the metrics, tests, and models all be science-driven; that is, to have them accurately represent the algorithms and implementations of a specific workload of interest.

The Performance Breakout Team established a flowchart for system integration performance evaluation that called out a series of specific stages (beginning at delivery), goals at each stage, and a suggested set of tools or methods to be used along the way. Such methods include the NERSC SSP and ESP metrics/tests for application and systemwide performance, respectively, NWPerf (a systemwide performance monitoring tool from PNNL), and a variety of low-level kernel or microkernel tests such as NAS Parallel Benchmarks, HPC Challenge Benchmarks, STREAM, IOR, and MultiPong. A key finding, however, is that many sites use rather ad-hoc, informal recipes for performance evaluation and the community could benefit from an effort to create a framework consisting of a set of standardized tests that provide decision points for the process of performance debugging large systems. Additional mutual advantage might be gained through the creation and maintenance of a central repository for performance data.

Charge to Breakout Group 3: Methods of Testing and Integration

There is a range of methods for fielding large-scale systems, ranging from self integration, cooperative development, factory testing, and on-site acceptance testing. Each site and system has different goals and selects from the range of methods. When are different methods appropriate? What is the right balance between the different approaches? Are there better combinations than others?

Report of Break Out Group #3

The major challenges in the testing and integration area are as follows:

1. Contract Requirements Balancing contract requirements and innovation with vendors. If the vendor is subject to risks, the vendor is likely to pad the costs and the schedule. A joint development model, with risks shared between the institution and vendor, may alleviate this but also places significant burdens on facilities. In order to be able to manage this and still reach their expectations, some faculties need more and different expertise. The cost of supporting this effort has to be borne by the facilities’ stakeholders An example of a procurement with lots of future unknowns is NSF track 1, with delivery 4+ years in the future. Here the NSF is actually funding the facilities to accumulate expertise to alleviate some of the risk. Suggestions for meeting this challenge:

- focus more on performance and less on detailed design description

- replace specific requirements with engineering targets and/or flexible goals

- have go/no-go milestones for the engineering targets, at which point you negotiate the next round of targets (this is especially useful if the vendor is in a development cycle with their product) or the system is multi-phased.

2. Testing: Vendors will never have systems as large as those installed at centers; so much of the testing will happen at sites. At the very least, however, vendors should have an in-house a system that is 10-15 percent of the size of their largest customer’s system. Suggestions for meeting this challenge:

- Vendors will need time on your machine. For example, at ORNL, Cray gets their full XT4 every other weekend, and half of the system on the alternate weekends.

- Need a way to swap in and out between the production environment and the test environment (ask the vendor for proof of the ability to do this) in an efficient manner.

- Share system admin tests across sites (just as we've started to share benchmarks) in the areas of:

  - swapping disks

  - managing large disk pools

  - managing system dumps

  - booting process

  - job scheduling (note: need to include job scheduling in integration testing)

  - NERSC ESP (http://www.nersc.gov/projects/esp.php)

- Need for at least one, if not multiple, development systems (one needs to be identical to the production system; ideal to have different development systems for systems and application work) that are sufficient in size and scope to be representative of a full system.

3. Lead times for procurements: This makes it difficult to develop performance criteria, as well as predict what performance will be. A process is needed to determine performance and milestone dates for solidifying the specifications. Another problem is that the longer a system stays in acceptance testing mode, the higher the cost both to the vendor and the site. Suggestions for meeting this challenge:

- Negotiate a milestone approach rather than one monolithic acceptance test

- In some cases, it may be useful to procure subcomponents and accept them separately, then federate them, perhaps allowing vendors to recognize revenue earlier. However, this approach should be used carefully, as it may be in conflict with Sarbanes-Oxley rules and also blurs lines of responsibility between which organization if responsible for performance and reliability.

4. Debugging problems at scale:For both the scientific users of systems and the system managers, many problems are not identified or detectable at smaller scales. This is particularly true for timing problems.  For the scientific users, the number of tools is limited (two debuggers exist for programs at scale) and complex to use. For system issues, there are no debugging tools, and often custom patches are needed to even get debugging information. Issues to consider:

- How to do fault isolation?

- How do you debug problems at scale when they only show up intermittently or after long run times?

- How to do quality control and consistency at scale (you can get inconsistent performance due to different batches of components)?

Suggestions to meet this challenge include

- Fund reliability and root cause analysis studies, particularly for system software. Finding root causes is typically difficult and expensive – requiring large scale resources at times. Specialized “deep dive” expertise might be established within the community – maybe at multiple sites – that can be deployed specifically to deal with such root cause analysis.

- Create new technology and more competition in the area of debugging tools. For many years, only one tool existed, and most vendors got out of the business of application debugging. The approaches that worked at 10-100’s processors become very difficult at 1,000 processors and impossible at 10,000 processors. New funding for debugging tools – both application and system – is critical.

- Funding to accumulate errors information is important. It was noted that the traditional approach of sharing error information and solutions between sites is not working any more. This is in part because most sites have multiple vendors, yet see similar problems, and because much of the software now in place is horizontally integrated. Hence, funding the effort to create, maintain and refine repositories of information is important.

- Use the influence of the general community to encourage/require the sharing of problems across sites with systems from the same vendors. Most vendors keep problem reporting private, and often multiple sites have to find and troubleshoot the same issue.

5. Determining when a system if ready for production: In some ways, “production quality” is in the eye of the beholder. What is useful and reliable to one application or user may not be to another. Issues include determining when to go from acceptance testing to production (suggest that acceptance testing only deal with systemic problems, not every last bug), and determining who is responsible for performance/stability when multiple vendors have different pieces.

A related issue is how to manage the responsibilities of having systems created and built by multiple vendors. Very few vendors have complete control over all the technology in their systems. Suggestions to meet this challenge:

- Use contracts that require the vendors to cooperate and that their piece has to work. Approach the system as a partnership (e.g., ORNL has a contract with CFS independent of the contract with Cray).

- Need more risk management and contingency strategies explicitly included in system planning and management. With multiple vendors, sites run the risk, and may explicitly decide to, become the integrator and assume some of the risk (“mutually assured risk”). There is a need to share more information about this as to the boundaries, management and contractual arrangements that work best. (Perhpas this can be a subject of the next workshop.)

6. What tools and technology do we wish we had? At busy sites, with multiple requirements, there are always things that would be good to have. Although these tool requirements are too much for any one vendor to provide, the HPC community could look to universities and laboratories to develop the frameworks that vendors can then plug into. All these areas are good candidates for stakeholder funding, even though they may not be “research”. Some of these are:

- Ability to fully simulate a system at scale before building it — better hardware and software diagnostics

- Hardware partitioning so that one partition cannot impact another partition

- Ability to virtualize the file system so different test periods do not endanger user data

- System visualization — a way to see what the whole system is doing (and display it remotely)

- Support for multiple versions of the operating system and the ability to quickly boot between them — tools that verify the correctness of the OS and the integrity of system files and that do consistency checking among all the pieces of the system

- System backups at scale in time periods that make backup tractable

- More holistic system monitoring (trying to see the forest despite the trees)

- Consolidated event and log management and the ability to analyze logs and correlate events. This must be provided in an extensible open framework.

- Parallel debugger that works at scale

- Better tools for dump analysis

- Parallel I/O test suite

- Ability to better manage large numbers of files

- More fault tolerance and fault recovery

Charge to Breakout Group 4: Systems and User Environment Integration Issues

Points to consider: Breakout session #2 looked at performance and benchmarking tools. While performance is one element of successful systems, so are effective resource management, reliability, consistency and usability, to name a few. Other than performance, what other areas are critical to successful integration? How are these evaluated?

Report of Break Out Group #4

The major areas addressed by the group included:

      - Effective Resource Management

      - Reliability

      - Consistency

      - Usability

1. Resource Management: Systems and system software remain primarily focused on coordinating and husbanding CPU resources. However, many applications and workloads find other resources equally or more critical to their effective completion. These include coordinated scheduling of disk space, memory and locations of CPUs in the topology. Resource management and human management of petascale disk storage systems may exceed the effort to manage the compute resources for the system. We need more attention to the implementation of disk quotas (and quotas in general) to manage data storage. Likewise, future topologies that have more limited bandwidth may benefit from tools such as job migration to help with scheduling and fault tolerance.

Considerations:

      - With current schedulers, can the sites effectively create policies that meet their user needs?

      - On large systems, what proportion of the resource should be allocated to the development-size (small) jobs for the user community?

  - Users are pushed to take advantage of the very large system, perhaps to the detriment of developmental jobs.

  - Integration of batch and interactive scheduling

2. Reliability: Reliability is a significant concern for petascale systems not only because of the immense number of components, but also because of the complex (almost chaotic) interactions of the components. Discussion focused on three areas: event management, RAS (remote access service) and system resiliency for the issues and suggestions.

Recording and managing events issues deal with acquiring and efficiently understanding the complex of the systems.  There is a critical need for a uniform framework for recording and analyzing events. This framework, which generated a significant discussion at the workshop, might possibly use API/XML tags for easier data sharing and analysis. Technical issues for such a framework include questions of granularity (core, CPU, node, or cluster) and who defines the levels of granularity (sites, vendors, etc.) The goal is to coordinate events that happen across multiple systems/subsystems. For example: Correlate batch job logs with other system events. Both asynchronous and synchronous event polling (proactive and reactive) need to be considered.

(This area may also be a topic for a future workshop.)

Suggested tools/technologies for this area include:

- Monitoring at appropriate levels (avoid overwhelming volumes that tend to be ignored)

- Developing tools that help process the large volumes of data to help forecast, detect, and provide forensic support for system anomalies. These tools would enable

- Root cause analysis tools

- Critical event triage tools

- Statistical analysis tools for analyzing events

- Failure prediction

- Resource tracking to have a mechanism for feeding these new resource management requirements back to the vendors.

-

Reliability, Availability and Serviceability (RAS) system: How much complexity and level of effort is introduced by the RAS system for these large systems? RAS systems have introduced many issues in large-scale systems and have taken significant effort to diagnose. On the other hand, they seem to play a key role in all system design. Issues about RAS being too complex, onerous and bulky are important to explore.

- In some cases, RAS subsystems have been observed to cause more problems than they solve. In other cases, complex, hardware-oriented RAS systems have been subverted by software that does not match the same level of responsiveness. Are extensions to current RAS systems adequately designed for petascale size systems?

- Most formal RAS study, and most common RAS features are based on hardware. Maybe because of the hard RAS features, systems often have the majority of their critical systemwide failures caused by software. Unfortunately, there is little data and less study of software failures in petascale systems.

- The major issue is what RAS features are required for petascale size systems? Conversely, what features work only at smaller scale, and can or should be discounted/discarded at larger scales? Again, there is a critical need to understand the software issues in addition to the hardware.

- Disk RAS is separate from the system RAS. Problems that affect one subsystem may affect the other system. With no integration, the identification of the error is much more complicated.

Suggestions for addressing these issues

- Root cause analysis that would efficiently respond to complex queries such as “What event triggered the other 10,000 alarms?”

- Correlation of events is very difficult given all currently disparate RAS systems (disk, network, nodes, system hardware and software)

- More holistic system monitoring tools. Per core monitoring? It’ll kill you.

- Correlation of performance events with reliability events

System Resiliency - From the system perspective, it is best to keep the compute node simple. This means few or none of the features seen in commodity or even special servers such as virtual memory with paging. When systems lose components, can they degrade gracefully? At what impact to the users? PNNL is attempting to identify failing components prior to loss (mitigation strategy), but this approach requires job migration which is not a common feature in today’s software world. A different approach would be to allocate a larger node or CPU pool than necessary so that if a node is lost, that work can be migrated to a ‘spare’ node.

Resiliency from the user perspective includes the tools/techniques the users need to create more fault-tolerant applications. Today, our applications are very fragile, meaning that the loss of one component causes the loss of all the work on all the components. This causes applications to put stress on other resources, such as when applications do “defensive IO” in order to checkpoint their work.

There are methods to allow applications to survive component outages and recover, such as journaling, work queues and duplication of function. None of these are used in HPC since they sacrifice performance for resiliency. Is it time at the petascale to change applications to do this?. Will CPUs be so cheap, it ibecomes feasible? How do we educate the users to write more fault-tolerant applications? Can you reconstruct lost data from nearest neighbors?

Suggestions to address resiliency issues are

- Fund research for new applications and algorithms that not only scale but also improve resiliency.

- Accept lower performance on applications to improve resiliency

Consistency: Large-scale systems can produce inconsistent results in terms of answers and run times. Inconsistency negatively impacts system effectiveness and utilization. From the system perspective, it becomes very expensive (and maybe impossible) for vendors to keep a completely homogeneous set of spare parts. When components are replaced, for whatever reason, the replacement frequently is slightly different (lot, firmware, hardware).

Consistency is also desired in the user environment. When a science code behaves differently the reasons may not be clear. It could be due to compiler changes, changing libraries or jitter in the system. If the user mistakenly guesses the run of a job incorrectly, it may take longer to be scheduled or, worse, it may be killed for going over its time limit. Either way, the user’s productivity is undermined.

Hence suggestions are:

- Sites may have to develop new maintenance strategies since it may not be possible to prevent heterogeneity of the system components over its life span.

- Configuration management tools to manage this component-level knowledge base, but which will be executed on a site-by-site, case-by-case basis, will be critical to understanding and predicting inconsistency

- Methods to allow a site to return to a previous state of the system will benefit users and sites once inconsistency is detected. This would have broad impacts across kernel, firmware upgrade processes that are currently used.

Usability: System reliability and environmental stability directly affect the perceived “usability” by the user community. Other features are necessary for a large-scale system to be usable by the science community. Access to highly optimizing compilers and math libraries at the petascale is key. Good parallel debugging tools are also important, along with integrated development environments such as the eclipse parallel tool kit platform. Essentially, tools that will help users understand job status and workflow management (When will it run? Why did it abort?, etc.) are needed.

A system with good performance balances will be important to supporting a range of science. This includes memory size and bandwidth, interconnect bandwidth and latenc,y and the number of threads or concurrency supported. Consistency of the environment across multiple systems (scheduler, file systems) contributes to usability.

Resource Management: Systems and user environments have not made much real progress in terms of system resource/system management software over the last 30 years. The scarcity of CPUs is no longer the issue for scheduling, but system still focus on that. Rather, bandwidth, disk storage, and memory use are the limiting factors. Even monitoring usage in these areas is difficult, let alone managing it. Can schedulers be made aware of machine-specific features that will impact performance of the code? XT series machines are a specific example. The location of the code on the machine will impact its performance because of bandwidth limitations in the torus links.

Job scheduling logs are underutilized. Error detection tools should be able to correlate system failures with jobs. There should be better ways to separate these job failures from user error or system issues. Job failure due to system failure should be calculable. In-house tools are being used at some sites to try to correlate batch system events with system events. This is limited and the algorithms are not sophisticated. For example, research has shown system failures in large systems often have precursor symptoms, but sophisticated analysis is needed to detect them. Little work has been funded in this area and few tools are available that may allow adaptive behavior (e.g., they don’t schedule work on that job, etc. until diagnostics determine failure cause). There are many issues, including how to deal with false positives. Managing multi-thousand-node log files is a challenge due to the sheer volume of data.

Research has given interesting hints of what may be possible. For example, statistical learning theory was used to analyze http logs and was shown to detect pending failures well before they occurred. Statistical methods are deployed by Google and Yahoo to address reliability and adaptive systems requirements.

Hard drive failure analysis is another area that offers substantial research issues, as well as practical issues to use in real environments. What forewarning technology exists? Will virtualization assist in any of the management issues?

Suggestions for these issues include:

- The community needs a tool that can analyze the logs, perhaps drawing from tools like LBNL’s Bro, which can analyze network traffic for anomalies that indicate attacks, etc. It is not possible for any single operational site or vendor can fund such research on their own, and new approaches are needed.

- There are basic research questions in the areas of artificial intelligence, data management, operating systems, statistics, reliability research, and human factors that need to be addressed before useful tools can be developed.

- Understanding failure modes is not well funded in large-scale computing. There is a little funding in the Petascale Data Storage Institute – a SciDAC project – but that is mostly focused on data.

Best Practices: The group developed a list of best practices that many sites use to address the challenges in the reliability arena. These include:

- Have a non-user test/development system that matches the hardware configuration of any large system. It can be used for testing new software releases, doing regression testing, and exploring problems. It is important the test/development system be identical in HW to the full system, as well as having all the same configuration components.  All the software components and layers are needed as well, albeit periodically at different versions.

- Trend analysis is important. One example of a problem cited was a system that showed performance degradation at 5 percent per month since reboot. This took a long term trend analysis effort to detect.

- Establish reference baselines of performance and services at the component level. This allows proactive testing and detection of anomalous conditions with periodic consistency checking at the component level

- Proactively check performance over time. The time periods and testing vary, but many problems that are difficult to detect early in the general workload have been found with proactive performance testing in a consistent (i.e., automated) manner

- Perform Regression Testing for all significant changes – both before the change on the test system and during system time, and after the change. (see Breakout #5 as well)

- File systems should be implemented with multipath I/O connections and redundant controllers. RAID arrays are almost mandatory for any large file systems. As the number of components in storage systems continues to increase it may be that RAID-5 is no longer sufficient.

- Multipath power connections to computing, storage and networking equipment from two independent panels or PDUs, even without UPSs, improves the ability for a site to continue operation through standard facilities repair and changes.

- Proactive memory resource management

System Deployment: Do not deploy subsystems until they are actually ready for deployment and the expected workload. The pressure for some use of new systems should be balanced by the need to provide a quality experience for the early science community.  Some metrics or parameters for successful integration may include:

- Are the users happy with the tools that are available to them to assist with their work?

- Middleware must be tested as it is expected to be used. For example, schedulers must be tuned to the requirements of the user community. Are there repeatable run times, queue wait times, etc. on the system?

- System management and user environment: Are there site-specific tools available that will help the users effectively use the system and understand problems?

- System Balance: What is the compute versus file system performance, network performance, etc.?

- Still no integration of CPU scheduling with disk scheduling. There’s never enough temp space, and there’s never enough bandwidth to scratch storage. Can users accurately forecast their temporary space requirements, when they still have difficulty forecasting their run time/CPU requirements?

Charge to Breakout Group 5: Early Warning Signs of Problems – Detecting and Handling

Fielding large scale systems is a major project in its own right, and takes cooperation between site staff, stakeholders, users, vendors, third party contributors and many more. How can early warning signs of problems be detected? When they are detected, what should be done about them? How can they be best handled to have the highest and quickest success? How do we ensure long-term success versus the pressure of quick milestone accomplishment? Will the current focus on formal project management methods help or hinder?

Report of Break Out Group #5

Each system is unique and may consist of many components that must all be successfully integrated, perhaps at a scale never before attempted. It may be built on-site without a factory test. Setting realistic schedules and meeting milestones can pose challenges. Risk assessment and management plans must be developed to deal with the uncertainties inherent in installing novel large-scale systems.

It is important to quickly detect and correct problems that arise during system integration.

The method for doing so can be somewhat of an art — “something doesn’t feel right” — based on experience. More well-defined procedures are desired, but the community does not have broad experience with formal project management procedures and tools. Project management processes have been imposed by funding agencies and are likely to remain. However, these have not yet proved to be effective tools for detecting and handling early warning signs of problems in the realm of HPC. It is not clear what are the most effective modifications to traditional PM methods to accommodate the needs of HPC.

Suggestions for addressing these issues include the following:

- A good management plan that measures overall progress is needed to guard against the perception that progress is being made solving day-to-day problems, while the number of problems is not decreasing. The plan should be able to retire risks systematically. The plan must have buy-in from sites, vendors and funding agencies. Paths for escalating problems to higher levels of management should be explicit and agreed upon by all parties. It has proven valuable to have site and vendor owners for identified major risks.

- Detailed tracking of individual components and failures, along with root cause analyses, can help identify problems and ensure component consistency across the system. Testing the functionality and performance of scientific applications should be part of the standard system tests and acceptance plans. The integration plan needs to contain an adequate number of agreed-upon milestones to ensure early detection of problems.

- While each installation is unique, it is valuable for sites to share experiences. Sites can exchange representatives to observe and advise during integration. (It should be possible to deal with issues if the plans are proprietary.) Outside review committees can be used. Workshops or community events sponsored by funding agencies can facilitate information-sharing, including making this workshop an ongoing event. An online community site would be useful.

- A hierarchy of project review meetings can serve as checks at different levels within organizations. Meetings between site and vendor technical staff should be encouraged, separate from management meetings.

With current revenue-reporting rules, there may be conflicts between vendors, who want a system accepted before a fiscal year deadline and under Sarbanes-Oxley rules, and sites, who want a well-tested and validated machine. The project plan should try to mitigate these conflicts as much as possible ahead of time and ensure success for all parties. Having a plan that tracks overall progress is important in this context.

Charge to Breakout Group 6: How to Keep Systems Running up to Expectations.

Once systems are integrated and accepted, is the job done? If systems pass a set of tests, will they continue to perform at the level they start at? How can we assure systems continue to deliver what is expected? What levels and types of continuous testing are appropriate?

Report of Break Out Group #6

The topics of discussion in Breakout Group 6 were how to detect changes in system performance and system health and integrity. All of the sites represented conduct some form of regression testing after upgrades to system software or hardware. Most of the sites do periodic performance monitoring using a defined group of benchmarks. Some of the sites do system health checking either at time of job launch or on a periodic basis via cron commands.

A major issue for petascale systems is how to manage the information collected by system monitoring. The amount of information generated by system logging and running diagnostics is hard to manage now – if current practices are continued, data collected on a petascale system will be so voluminous that the resources needed for storing and analyzing it will be prohibitively expensive.

Suggestions to help address these issues include:

- Identified needs are standardizing and intelligently filtering system log data, an API or standard data format for system monitoring, and the development of tools for analyzing and displaying system performance and health using the standard formats and API.

The participants in the breakout session started developing a draft of best practices for continuous performance assessment including suggested techniques and time scales.

List of Attendees

Bill Allcock, Argonne National Laboratory

Phil Andrews, San Diego Supercomputer Center/UCSD

Anna Maria Bailey, Lawrence Livermore National Laboratory

Ron Bailey, AMTI/NASA Ames

Ray Bair, Argonne National Laboratory

Ann Baker, Oak Ridge National Laboratory

Robert Balance, Sandia National Laboratories

Jeff Becklehimer, Cray Inc.

Tom Bettge, National Center for Atmospheric Research (NCAR)

Richard Blake, Science and Technology Facilities Council

Buddy Bland, Oak Ridge National Laboratory

Tina Butler, NERSC/Lawrence Berkeley National Laboratory

Nicholas Cardo, NERSC/Lawrence Berkeley National Laboratory

Bob Ciotti, NASA Ames Research Center

Susan Coghlan, Argonne National Laboratory

Brad Comes, DoD High Performance Computing Modernization Program

Dave Cowley, Battelle/Pacific Northwest National Laboratory

Kim Cupps, Lawrence Livermore National Laboratory

Thomas Davis, NERSC/Lawrence Berkeley National Laboratory

Brent Draney, NERSC/Lawrence Berkeley National Laboratory

Daniel Dowling, Sun Microsystems

Tom Engel, National Center for Atmospheric Research (NCAR)

Al Geist, Oak Ridge National Laboratory

Richard Gerber, NERSC/Lawrence Berkeley National Laboratory

Sergi Girona, Barcelona Supercomputing Center

Dave Hancock, Indiana University

Barbara Helland, Department of Energy

Dan Hitchcock, Department of Energy

Wayne Hoyenga, National Center for Supercomputing Applications (NCSA)/University of Illinois

Fred Johnson, Department of Energy

Gary Jung, Lawrence Berkeley National Laboratory

Jim Kasdorf, Pittsburgh Supercomputing Center

Chulho Kim, IBM

Patricia Kovatch, San Diego Supercomputer Center

Bill Kramer, NERSC/Lawrence Berkeley National Laboratory

Paul Kummer, STFC Daresbury Laboratory

Jason Lee, NERSC/Lawrence Berkeley National Laboratory

Steve Lowe, NERSC/Lawrence Berkeley National Laboratory

Tom Marazzi, Cray Inc.

Dave Martinez, Sandia National Laboratories

Mike McCraney, Maui High Performance Computing Center

Chuck McParland, Lawrence Berkeley National Laboratory

Stephen Meador, Department of Energy

George Michaels, Pacific Northwest National Laboratory

Tommy Minyard, Texas Advanced Computing Center

Tim Mooney, Sun Microsystems

Wolfgang E. Nagel, Center for Information Services and High Performance Computing ZIH, TU Dresden, Germany

Gary New, National Center for Atmospheric Research (NCAR)

Rob Pennington, National Center for Supercomputing Applications (NCSA)/University of Illinois

Terri Quinn, Lawrence Livermore National Laboratory

Kevin Regimbal, Battelle/Pacific Northwest National Laboratory

Renato Ribeiro, Sun Microsystems

Lynn Rippe, NERSC/Lawrence Berkeley National Laboratory

Jim Rogers, Oak Ridge National Laboratory

Jay Scott, Pittsburgh Supercomputing Center

Mark Seager, Lawrence Livermore National Laboratory

David Skinner, NERSC/Lawrence Berkeley National Laboratory

Kevin Stelljes, Cray Inc.

Gene Stott, Battelle/Pacific Northwest National Laboratory

Sunny Sundstrom, Linux Networx, Inc.

Bob Tomlinson, Los Alamos National Laboratory

Francesca Verdier, NERSC/Lawrence Berkeley National Laboratory

Wayne Vieira, Sun Microsystems

Howard Walter, NERSC/Lawrence Berkeley National Laboratory

Ucilia Wang, Lawrence Berkeley National Laboratory

Harvey Wasserman, NERSC/Lawrence Berkeley National Laboratory

Kevin Wohlever, Ohio Supercomputer Center

Klaus Wolkersdorfer, Forschungszentrum Juelich, Germany

List of priorities from attendees based on a ranking algorithm.

| Description | Summary ranking |
| --- | --- |
| Provide methods for regular interaction between peer centers to avoid potential pitfalls and identify best practices. | 187 |
| Consolidated event and log management with event analysis and correlation. Must be an extensible, open framework. Common format to express system performance (at a low level), health, status, and resource utilization (e.g <machine name=“franklin”>; <cab | 142 |
| Tools for ongoing “Intelligent” syslog / data reduction and analysis. | 123 |
| Develop methods to combine machine and environment monitoring. | 113 |
| Ability to have multiple versions of the OS that can be easily booted for testing and development. Ability to do rolling upgrades of the system and tools. Can you return to a previous state of the system? Very broad impacts across kernel, firmware, etc. | 113 |
| Develop standard formats and ability to share information about machines and facilities (Wiki?). Community monitoring API (SIM?) | 112 |
| Develop better hardware and software diagnostics | 108 |
| Develop tools to track and monitor message performance (e.g. HPM/PAPI for the interconnect and I/O paths, hybrid programming models) | 105 |
| Create better parallel I/O performance tests and/or a Parallel I/O test suite | 101 |
| Funded Best Practices Sharing (Chronological list of questions and elements of project plan, Top 10 Risk Lists, Commodity equipment acquisition / performance) | 99 |
| Better ways to visualize what the system is doing with remote display to a system administrator for more holistic system monitoring. | 96 |
| Visualization and Analytics tools for log and performance data. Tool that can analyze the logs, perhaps drawing a parallel to Bro, which can analyze network traffic for anomalies that indicate attacks, etc | 90 |
| Invite peer center personnel to review building design plans to achieve as much input as possible and so reviewers can benefit as well. | 86 |
| Tools for storage (Disk) Systems management and reliability | 85 |
| Develop/identify computer facility modeling and analysis software (Air flow, cooling system, etc. – e.g Tileflow) | 81 |
| Develop automated procedures for performance testing | 81 |
| Share problem reports with all sites – a vendor issue rather than a site issue. | 80 |
| Improved parallel debugger for large scale systems including dump analysis | 77 |
| Develop tools to verify the integrity of the system files and to do consistency checking among all the pieces of the system. | 67 |
| Develop accurate methods for memory usage monitor/OS intrusion | 65 |
| Tools to monitor performance relative to energy power draw | 63 |
| Failure data fusion and statistical analysis | 60 |
| Develop realistic interconnect tests | 59 |
| Scalable configuration management | 58 |
| Job failure due to system failure should be calculable. In house tools are being used in some cases to try and correlate batch system events with system events. | 57 |
| Share (Sanitized) Project Plan experience among sites as part of project closeout – RM activities required | 56 |
| Implement facility sensor networks in computer rooms including analysis and data fusion capabilities | 55 |
| Develop accurate performance models for non-existent systems including full system including I/O, interconnects, software | 55 |
| Develop tools to measure real Bit Error Rate (BER) for interconnects and I/O | 52 |
| Developing improved methods of backing up a systems of this size | 52 |
| Develop matrix to correlate the four major facility categories (Space, Power, Cooling, Networking) with each of these phases of a facility for Greenfield (new), Retrofit, Relocate, Upgrade for planning purposes. | 48 |
| Create the ability to fully simulate a full system at scale without having to build it (e.g UCB RAMP) | 46 |
| Develop ways to receive real data for power consumption from vendors | 42 |
| Hard partitioning of systems so one partition cannot impact another. Virtualized the I/O partition so that it can be attached to multiple compute partitions. | 42 |
| Have external participation in proposal and plan reviews | 42 |
| Fund studies about systemic facility design (What voltage? AC or DC? CRAC Units, Etc.) including the level of detail needed for monitoring? | 41 |
| Statistical analysis of logs can detect pending failures. Is deployed by Google, Yahoo to address reliable and adaptive systems requirements. Currently based on http:, but may be extensible to this situation. | 40 |
| Coordinate scheduling of resources in addition to CPUs | 39 |
| Share WBS, RM, Communications Plans, etc. among sites | 37 |
| Improve Project Management expertise in organizations | 36 |
| Create a framework with general acceptance by most of the community consisting of a set of tests that provide decision points on the flow chart for debugging | 17 |
| Benchmarks in new programming models (UPC, CAF, …) | 17 |
| Reporting that shows just the important (different) areas in the machine | 15 |
| Develop the methods and roles for statistician with PSI projects | 6 |
| Configuration management tools can manage this component-level knowledge base, but will be executed on a site-by-site, case-by-case basis. | 2 |